## Slide 1
StreamDevice

## Slide 2: What is StreamDevice?
EPICS module used to define string-based communication protocols between EPICS records and devices with a serial interface (serial port, Ethernet)
  E.g. Message sent: “V?”; Message received: “V=2.1”
Simple configuration, no programming required
Based on plain text protocol files, easy to understand
Uses ASYN driver to handle the low-level communication:
  Thread handling, Proper resource locking, Queueing (by priority)
All documentation: https://paulscherrerinstitute.github.io/StreamDevice/

## Slide 3: Architecture
Protocol file includes a set of protocols
  A protocol is a set of “instructions” how to make a particular data exchange with a particular device
Records use protocols to configure how they function
Records communicate with HW device by exchanging the messages described in their assigned protocol via an AsynPort Driver
IOC
Protocol file (*.proto)
EPICS record
AsynPort
Driver
Device

## Slide 4: ASYN Port Driver Configuration
AsynPort is initialized in IOC start file: epics/iocBoot/<ioc>/userPreDriverConf.cmd
IP connection: drvAsynIPPortConfigure ("DEV1", "192.168.1.212:8080") Creates a connection called "DEV1" with a network device reachable at 192.168.1.212 over port 8080
Serial connection: drvAsynSerialPortConfigure ("DEV2", "/dev/ttyS1") Creates a connection called "DEV2" with a serial device connected to /dev/ttyS1
Optional ASYN parameters (line terminators, serial communication parameters…) may be specified with other commands
For debugging, the ASYN trace mask can be used to output to shell exactly what is being transmitted: asynSetTraceMask("DEV1",-1,0x9); asynSetTraceIOMask("DEV1",-1,0x2)
Check asynDriver.h for details
IOC
Protocol file (*.proto)
EPICS record
AsynPort
Driver
Device

## Slide 5: Record Configuration
Two fields are used to tell a record to use Stream Device
Device Type (DTYP): field (DTYP, "stream")
Either Input (INP) or Output (OUT): field (INP, "@protoFile.proto getFrequency DEV1") field (OUT, "@protoFile.proto setFrequency DEV1")
First example tells input record to acquire its value using protocol getFrequency, specified in the file protoFile.proto, from device connection DEV1
Second example tells output record to send its value using protocol setFrequency, specified in the file protoFile.proto, to device connection DEV1
Record types that may use StreamDevice out of the box: ai, ao, bi, bo, mbbi, mbbo, mbbiDirect, mbboDirect, longin, longout, int64in, int64out, lsi, lso, stringin, stringout, aai, aao, waveform, calcout, scalcout
Others require additional support
IOC
Protocol file (*.proto)
EPICS record
AsynPort
Driver
Device

## Slide 6: Including Protocol Files in the Project Build
Protocol files don’t need to be compiled, but the IOC needs to know where to find them during startup.
Place protocol files in: epics/<Device>App/Db/
  with *.proto extension
They are automatically included in the build
Or: define STREAM_PROTOCOL_PATH to where the files are kept.
IOC
Protocol file (*.proto)
EPICS record
AsynPort
Driver
Device

## Slide 7: Protocol Files
Plain text ASCII files containing a set of protocols
Each protocol has a name and a sequence of commands
  in string; - reads message that matches “string”
  out string; - sends message that matches “string”
  others: wait, event, exec, disconnect, connect
“Strings” are matched using format converters
  doubles or floats: %f, %e, %E, %g, %G
  shorts, ints or longs: %d, %i, %u, %o, %x, %X
  strings or chars: %s, %c
  enumerations: %{string0|string1|...}
  others: %[charset], %b, %Bzo, %r, %R, %D, %<checksum>, %/regex/, %#/regex/subst/, %m, %T(timeformat)
Optional width and flags can modify behavior of format converters
  Width specifies number of characters string should have
  Flags: *(skip), #(format), +(positive int prefix), 0(pad), -(left justify), ?(allow fail), =(compare), !(impose width)

## Slide 8: Features
Protocol nesting – one protocol may call another
Redirection – protocols may read/write from/to other records and/or fields (often not a good practice, but possible)
System variables – preset variables (can be local or global): LockTimeout, WriteTimeout, ReplyTimeout, ReadTimeout, PollPeriod, Terminator, OutTerminator, InTerminator, MaxInput, Separator, ExtraInput
User variables – free to customize, called with '$' prefix
Arguments – arguments can be passed from the record to the protocol it calls (up to 9, called with \$1..\$9)
Exception handlers – clauses that are called only when certain conditions are met: @mismatch, @writetimeout, @replytimeout, @readtimeout, @init

## Slide 9: Example Protocol File
Terminator = CR LF; # sets line terminators for both inputs and outputs to "\r\n"
f = "FREQ"; # User variable: sets f to "FREQ" (including the quotes)
f1 = $f " %f"; # User variable: sets f1 to "FREQ %f"
getFrequency { # ai could call this using INP="@protoFile.proto getFrequency DEV1"
out $f "?"; # same as: out "FREQ?";
in $f1; # same as: in "FREQ %f";
}
setFrequency { # ao could call this using OUT="@protoFile.proto setFrequency DEV1"
out $f1; # same as: out "FREQ %f";
@init { getFrequency; } # Exception handler calling another protocol: initial sync
}
getSwitch { # bi could call this using INP="@protoFile.proto getSwitch DEV1"
out "SW?"; in "SW %{OFF|ON}"; # if input is "SW OFF", VAL=0, if input is "SW ON", VAL=1
}
setSwitch { # bo could call this using OUT="@protoFile.proto setSwitch DEV1"
out "SW %{OFF|ON}"; # if VAL=0, send "SW OFF“, if VAL=1, send "SW ON"
@init { getSwitch; } # Exception handler calling another protocol: initial sync
}
move { out "\$1 GOTO %d"; } # ao could call this using OUT="@protoFile.proto move(X) DEV1"
debug { # Generic command for stringout record: any string written to
ExtraInput = Ignore; # … record’s VAL field is sent to device, any reply from device will
out "%s"; in "%39c" # … be written to record’s VAL field cropped at 39 characters.
}

## Slide 10: Messages Don’t Get Mixed Up!
Use case: Two records that use similar protocols for the same device are triggered to process at (almost) the same time
Record A protocol: { out “V PS1?”; in “%f”; }
Record B protocol: { out “V PS2?”; in “%f”; }
If both output messages are sent to the same device at the same time, how will the responses not get mixed up?
  Asyn Driver sends the first output message it receives (either A or B).
  Second output message gets buffered in a queue and doesn’t get sent (yet).
  Only once the first protocol is completed (a proper reply is received within the timeout), the second output message gets sent automatically.
ASYN takes care of everything!

## Slide 11: Summary
StreamDevice offers universal support to integrate all message-based devices
ASYN layer takes care of the low-level communications handling and provides out-of-the-box support for most low-level drivers: serial, TCP/IP, VXI-11, IEEE-488, …
Only configuration, no coding
Protocols are reloadable  Faster development
Support for common record types
Extendable:
  Write your own format converters
  Write support for other record types
  Use StreamDevice with other non-Asyn low-level drivers
However:
  Not a programming language (no for, if, etc.)
  Everything is a string (no other datatypes, just format converters)
  Line terminators can cause headaches (use Asyn Trace Mask for debugging!)
  Important to configure SCAN fields properly in accordance to record behavior
  Although quick to setup, can take time to make fail-safe (80/20 rule!)

## Slide 12
Thank You for Your Attention!